## Slide 1: Life Safety & Fire Code Jeopardy
Select a point value to begin

## Slide 2
Jeopardy Game Board
Fire Suppression Systems
Emergency Power Supply Systems
Egress Requirements
Fire Alarm
Miscellaneous
100
200
300
400
500
100
200
300
400
500
100
200
300
400
500
100
200
300
400
500
100
200
300
400
500

## Slide 3
According to NFPA 25, fire sprinkler gauges must be tested or replaced every ___ years.
Answer: 5 years
Return to Board

## Slide 4
According to NFPA 13, what is the minimum allowable distance from any obstruction to a pendant sprinkler deflector?
Answer: 18”
Return to Board

## Slide 5
According to NFPA 25, what is the required frequency for Fire Sprinkler Internal Pipe Inspections?
Answer: 5 years
Return to Board

## Slide 6
According to NFPA 25, what is the minimum run time for an electric motor-driven fire pump during the weekly churn test?
Answer: 10 minutes
Return to Board

## Slide 7
According to NFPA 13, what is the minimum amount of spare sprinkler heads required for each standard sprinkler head type with fewer than 300 used in the building?
Answer: 6
Return to Board

## Slide 8
According to NFPA 110, what is the minimum duration of a monthly generator load test?
Answer: 30 minutes
Return to Board

## Slide 9
According to NFPA 110, a 4-Hour Generator Load Test must be performed at intervals not exceeding ___.
Answer: 36 months (3 years)
Return to Board

## Slide 10
According to NFPA 110, what is the maximum allowable time for an Automatic Transfer Switch to transfer to emergency power after a power loss?
Answer: 10 seconds
Return to Board

## Slide 11
For an emergency power supply system, what is the minimum allowable time for a retransfer delay on the automatic transfer switch?
Answer: 5 minutes
Return to Board

## Slide 12
According to NFPA 110, a Diesel Fuel Analysis must be completed at least ___.
Answer: Annually (every 12 months)
Return to Board

## Slide 13
According to NFPA 101, what is the maximum allowable delay of egress that may be approved by the AHJ?
Answer: 30 seconds
Return to Board

## Slide 14
According to NFPA 101, what is the correct verbiage for delayed egress signage?
Answer: “PUSH UNTIL ALARM SOUNDS. DOOR CAN BE OPENED IN 15 SECONDS.”
Return to Board

## Slide 15
According to NFPA 101, what is the maximum allowable abrupt change in elevation on a walkway surface?
Answer: ¼”
Return to Board

## Slide 16
According to NFPA 101, when initiating a delayed egress device, the force shall not be required to be continuously applied for more than ___.
Answer: 3 seconds
Return to Board

## Slide 17
According to NFPA 101, the maximum force required to release a delayed egress locking system cannot exceed how many pounds?
Answer: 15 pounds
Return to Board

## Slide 18
According to NFPA 101, a fire watch must be conducted if a fire alarm system is out of service for planned maintenance for more than ___ hours in a 24-hour period.
Answer: 4
Return to Board

## Slide 19
According to NFPA 72, Smoke Detector Sensitivity Testing must be performed within 1 year of installation and afterwards at intervals not to exceed ___.
Answer: 2 years
Return to Board

## Slide 20
According to NFPA 72, what is the minimum clearance required around a fire alarm manual pull station?
Answer: 36”
Return to Board

## Slide 21
According to NFPA 72, what is the minimum and maximum height a fire alarm manual pull station must be from the finished floor?
Answer: 42” – 48”
Return to Board

## Slide 22
According to NFPA 72, a fire alarm manual pull station must be located with ___ of an egress door.
Answer: 5’
Return to Board

## Slide 23
According to NFPA 80, what is the minimum required inspection frequency for fire doors?
Answer: Annually (12 months)
Return to Board

## Slide 24
What rating must a power strip have to be used in an Assisted Living/Memory Care apartment?
Answer: UL1363
Return to Board

## Slide 25
According to NFPA 80, what is the maximum allowable gap for wood fire doors on the top and sides?
Answer: 1/8”
Return to Board

## Slide 26
According to NFPA 80 and NFPA 105, link fire dampers present in Assisted Living buildings must be inspected/tested within 1 year of installation and afterwards at intervals not to exceed ___.
Answer: 4 years
Return to Board

## Slide 27
According to NFPA 10, what is the maximum allowable distance to a fire extinguisher for ordinary combustible hazards?
Answer: 75 feet
Return to Board

## Slide 28: Thanks for Playing!
Great job!